## Slide 1
Experimental study of energy efficiency of CO2 hydrate slurry in a coil heat exchanger
Laurence FOURNAISON,
Thomas Dufour(PhD), Hong Minh HOANG, Véronique OSSWALD, Jérémy OIGNET, Pascal CLAIN,, Anthony DELAHAYE,

## Slide 2
Aim and context
Cold production:
    17 % of world energy consumption
    8 % GES:
Prospection:
Increase of efficiency
Reduction of refrigerant use
F-GAS regulation

## Slide 3
Secondary refrigeration with thermal energy storage
Aim and context
Terminal unit : Heat exchanger
Dissociation, Heat release, Efficiency?

## Slide 4
  Excès de CO2
Latent heat : 374 kJ/kg
Hydrate domain : 272 K to 284 K
Pressure : 10 to 45 b
CO2 hydrate slurry
  Ice slurry
  (Stamatiou et al., 2005)
CO2 hydrate

## Slide 5
Heat transfer coefficient : > 2 times pure water
Design of the heat exchanger:
Reduce length when increasing solid fraction
Higher ice content increase viscosity
Heat exchange with hydrate slurry
Optimization: Solid content versus tube length

## Slide 6
Experimental device and protocol

## Slide 7
Experimental device
Mass flow
Temperature
Pressure
Viscosity : capillary viscosimeter
Heat transfer coefficient : heating tube

## Slide 8
Counter flow heat exchanger
4 thermocouples :
Inlet/outlet water, slurry
The heat exchanger
Slurry
Hot water
Din : 7,7 mm
Dex : 9,5 mm

## Slide 9
P: 27 bar,
Thot:293 K;
wt: 12%
Protocol

## Slide 10
In house software: wt = f(T, P, xgas)
Hydrate content
wt increase higher energy available, higher heat transfer coefficient +
higher viscosity -

## Slide 11
Energy release and pressure drop
Hot water side:
Slurry side:
Heat Exchanger efficiency
Pumping power
Global performance efficiency

## Slide 12
Experimental results
Hydrate Flowrate: up to 160 kg.h-1, xhyd: 0 to 12 %
Hot Fluid Temperature: 283-293 K ; 58 kg.h-1

## Slide 13
Heat exchanger performance
Higher efficiency with slurry

## Slide 14
Pressure drop
Pressure drop increases with mass flow rate and solid fraction

## Slide 15
Global performance of the heat exchanger
Higher performance with: hot fluid
12 % solid fraction

## Slide 16
Conclusions
Hydrates enhance the heat exchange thanks to the increase of the temperature difference between cold and hot fluids provided by hydrate melting
While an increase of the pressure drop was observed for slurry due to a higher viscosity, it was possible to obtain a lower pressure drop than water by reducing the slurry flowrate
Hydrate slurry provides better efficiency than water since the increase in heat exchange overcomes the pumping power rise
Optimal solid fraction is found between 5 and 8 wt%; the optimal value shifted to higher fraction for higher power demand
Issue concerning hydrate dissociation

## Slide 17
Thank you for your attention
Projet Crisalhyd
Experimental and modelling study of energy efficiency of CO 2 hydrate slurry in a coil heat exchanger
Dufour, T., Hoa,g,H.M., Oignet, J., Osswald, V., Fournaison, L., Delahaye, A.
Applied Energy, Volume 242, 15 May 2019, Pages 492-505